Section Cover Page

Section 05301 1999-09-13 Metal Decking

Use this Section to specify requirements for metal decking, including floor decking and roof decking.

This Master Specification Section contains:

.1	This Cover Sheet

.2	Specification Section Text:

1.	General

1.1	Design Criteria

1.2	Reference Standards

1.3	Shop Drawings

1.4	Design

2.	Products

2.1	Materials

3.	Execution

3.1	Fabrication

3.2	Erection

Applicable Standards:

.1	ASTM A653M-96	Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot Dip Process

.2	CAN/CGSB-1.181-92	Ready-Mixed Organic Zinc-Rich Coating

.3	CSA S136-94	Cold Formed Steel Structural Members

.4	CSA W59-M1989	Welded Steel Construction (Metal Arc Welding)

These reference documents may be available for reference purposes in the Technical Resources and Standards Division Library, Alberta Infrastructure, 3rd Floor, 6950 - 113 Street, Edmonton; Telephone: (780) 427-7924.

1.	General

1.1	DESIGN CRITERIA

.1	Design of metal decking shall be in accordance with CSA S136-94.

1.2	REFERENCE DOCUMENTS

.1	Comply with applicable requirements of CSA S136-94.

.2	Except where otherwise specified, comply with applicable requirements of Canadian Sheet Steel Building Institute standards.

.3	Do welding in accordance with CSA W59-M1989.

1.3	SHOP DRAWINGS

.1	Comply with requirements of Division 1.

.2	Shop drawings shall indicate decking plan, joints, anchorages, supports, projections, opening and reinforcement, details and accessories.

2.	Products

2.1	MATERIALS

.1	Sheet Steel:  to ASTM A653M-96, zinc coated to [Z275] [ZF075] coating designation.

.2	Touch-Up Primer for Galvanized Steel:  zinc-rich, organic, ready mixed, to CAN/CGSB-1.181-92.

3.	Execution

3.1	FABRICATION

.1	Fabricate deck sections to CSA S136-94 and to dimensions indicated on drawings.

.2	Provide a male and female lip for each section of steel deck.

3.2	ERECTION

.1	Reinforce steel deck openings shown on the drawings unless otherwise noted.

.2	Structurally support all edges of openings cut into the deck.

.3	Install decking according to design sheet widths and depths. Correct sheet spread during installations.

.4	Button clinch sidelaps of adjacent sections at not greater than 600 mm on centre and at each end of a section, 25 mm clear of the lip ends.

.5	Connect steel deck to supporting member by 20 mm diameter plug welds at 300 mm on centre.

.6	Make connection welds by burning through deck with welding electrode and follow by puddling in the burned hole.

.7	Weld steel decking side sections running parallel to a framing or supporting member with 20 mm diameter plug welds at not greater than 750 mm on centres with a weld at each end of the sections, 25 mm clear of the section end.

.8	Attach metal cell closures at locations required to contain poured concrete, roof boundaries, and around openings in deck.

.9	Wire brush, clean and touch-up welds and scarred areas on top surfaces of metal decking with touch-up primer.

END OF SECTION